SECTION 11 40 00

AIR CURTAINS

Berner Drive-Thru Unit 3 Series (DTU03) air curtains (a.k.a. air doors) are designed to be competitively priced for indoor use on drive-thru windows.  They are suitable for openings up to 26 in (66.0 cm) wide in single modules (tandem mount for wider openings), with window heights up to 36 in (91.4 cm) for environmental separation and insect/fume control.

### Air curtains provide environmental separation at openings by reducing the infiltration of unconditioned air, fumes, dust, and humidity.  Optimum protection is provided when units are mounted flush to the wall and as close to top of the opening as possible.   To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

Series DTU03 model air curtains can be wall mounted or ceiling mounted with the “Mount Anywhere” bracket system. Electric heated units shall be installed indoors only and require – a minimum clearance of 18 in (45.7 cm) between the bottom of unit and the counter and 4 in (10.2 cm) between sides and top of the unit and any combustible material.

Edit guide specification to include only information specific to your project. Delete or add text, select appropriate bracketed phrases, and fill in blanks as required. Go to Berner catalog or website to select specific models and sizes that are required for project and to obtain data necessary to edit this document.

Coordinate specification with information shown on project drawings and schedules. In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules. Cross check mechanical and architectural drawings.

### This guide specification is available in word processing format at www.berner.com.  Turn on “Hidden Text” function in your word processor to display “Specifier Notes.”

For additional information or name of Berner representative in your area, call Berner International Corporation at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.berner.com. A selection guide is available at www.berner.com to suggest models appropriate for typical applications.

GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

Air curtains[, electric heated].

[Insert item description.]

RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air curtain must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to be field painted.  Protect electric contacts and moveable parts from paint.

Section 09 91 00 - Painting:  Field applied finishes.

Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

REFERENCE STANDARDS

Air Movement & Control Association International, Inc. (AMCA):

AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.

AMCA 220 - Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings.

AMCA 222 - Application Manual for Air Curtain Units.

National Electrical Manufacturers Association (NEMA):

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

Underwriters Laboratories (UL):

UL 507 - Electric Fans.

UL 2021 - Fixed and Location-Dedicated Electric Room Heaters.

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for [____________] including:

[_____________________.]

Rated capacities.

Operating characteristics.

Accessories.

Options.

Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

Indicate dimensions, weights, loads, clearances required, location and size of field connections.

Provide wiring diagrams for power, signal, and control wiring.

Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

Warranties:  Sample of special warranties.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Specifier Note:  Retain the following paragraph if specifying the ambient type of air curtain in this section.

Comply with AMCA 220, "Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings," for airflow, outlet velocity, and power consumption.

Certification:

Unheated and electric heated units to be UL Listed in the United States and Canada.

DELIVERY, STORAGE AND HANDLING

Deliver air curtains in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

WARRANTY

Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

One-year limited warranty for heated and unheated units.

PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International Corporation, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

Substitutions are not permitted.

Substitutions will be considered under provisions of Section 01 60 00.

AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are not required.

Acceptable Products:  Berner Drive-Thru Unit 03 Model [DTU03 Ambient] [DTU03 Electric Heated].

Construction:  Provide factory-assembled units of sufficient structural strength to be supported from ends without intermediate support. Ship units completely assembled.

Cabinet:

Material and Finish: Aluminum base frame with clear satin anodized finish.

Dimensions:  Not to exceed 6 in (15.2 cm) high by 7.75 in (19.7 cm) deep.

Specifier Note:  Retain only the mounting method required for a specific project in the following subparagraph and delete the others.

Mounting:  Provide for [wall] [suspended] mounting.

Service Access: Removable screen.

Motors:  1/12-hp, 2950 RPM, single phase, single speed, Open Frame, foot mounted, continuous duty, with internal thermal-overload protection, and permanently lubricated sleeve bearings.

Fans:  Balanced forward curved type, double inlet, mounted in matched fan housings.  Manufacture wheels and housings from galvanized steel; provide housings with powder coated finish.

Discharge Nozzles:

Provide uniform velocity across width of air curtain.

Aperture:  1.125 in (2.9 cm) slot by width of air curtain.

Vanes: 0.25 in (0.6 cm) minimum height; constructed of airfoil-shaped aluminum extrusions.

Inlet:

Location: Front.

Screen:  Staggered perforated pattern constructed of aluminum.

Air Inlet Filters:  Re-cleanable type constructed of aluminum with “No Tool” filter removal.

Adjustment Hardware:  Standard mounting hardware shall enable unit rotation a minimum of plus or minus 20 degrees to direct airflow for proper operation.

Electrical Connection:  Factory-installed cord and plug standard.

Specifier Note:  Retain the following article if heated units are required for a specific project.

HEATING ELEMENTS

Electric Heating Coil:  UL-approved, factory-mounted, factory-wired, thermally-protected, galvanized steel frame.

Helical coil with point suspended elements, single phase circuit.

Thermal Cutout: Locks out electric heaters when prolonged abnormal over-temperature conditions exist.

CONTROLS

Specifier Note:  Retain one of the following two paragraphs and delete the remaining one.

Switching:

Specifier Note: Retain the following subparagraph for use with unheated models.

Manual Switch:  Factory installed “Fan On-Off” selector switch rated 120 volt single phase.

Manual Switch:  Factory-installed “Fan On-Off-Fan & Heat” selector switch rated 120 volt single phase.

MOUNTING ACCESSORIES

Specifier Note:  Show mounting brackets on Drawings if required.

Provide brackets and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

Fabricate mounting accessories from black powder coated aluminized steel.

Specifier Note:  Retain the following subparagraph when the unit is mounted to the ceiling and longer brackets are needed to allow unit to be positioned at the top of the window.

Fabricate adjustable height mounting brackets of black powder coated aluminized steel to allow for mounting distance of up to 9 in (22.8 cm).

EXECUTION

EXAMINATION

Verify that door frame and adjacent construction are installed correctly and are ready to receive work of this Section.

Verify that utilities are in correct location and are of correct capacities for specified products.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

Securely install air curtains plumb, level, and as close as practical to top of opening and face of wall.

CONNECTIONS

Connect air curtain to utilities as specified in other Division 26 sections.

FIELD QUALITY CONTROL

Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Test and operate air curtain to be sure that it performs as intended.

ADJUSTING

Specifier Note: Delete the optional text in the following paragraph if not required for a specific project.

Adjust unit position to direct nozzle discharge air towards outside [unless otherwise required].

CLEANING

Clean air curtain prior to commissioning.

Repair or repaint damage to finishes on exposed-to-view surfaces.

SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

Test and operate air curtains to ensure that they perform as intended.  Adjust unit position to direct nozzle discharge air towards outside [unless otherwise required].

DEMONSTRATION

Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2019 Berner International Corporation.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Revd 06/2019