SECTION 23 34 33

AIR CURTAINS

Berner Series Industrial Direct Drive 16 (IDC16) and Industrial Belt Drive 16 (IBC16) air curtains (a.k.a. air doors) are designed for industrial applications such as service and dock doors. They are suitable for opening heights up to 16 ft (487.7 cm) for environmental separation and up to 14 ft (426.7 cm) for insect control.

Air curtains provide environmental separation at openings by reducing the infiltration of unconditioned air, fumes, dust, and humidity. At exterior openings, they can resist winds up 10 MPH (16 KPH) and are generally mounted on the inside of buildings. During cold seasons warm air that has risen towards ceiling is recirculated; they can also be used at interior openings such as doors to coolers or clean rooms.  Optimum protection is provided when units are mounted flush to the wall and as close to top of door opening as possible.   To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

Series IDC16 and IBC16 model air curtains have integral HP motors.  They can be wall mounted or suspended from the ceiling.  Electric heated units shall be installed indoors only and require – a minimum clearance of at least 6 ft (182.9 cm) between the bottom of the unit and the floor, a minimum of 8 in (20.3 cm) between the top and ceiling and 1 in (2.5 cm) between the sides and any combustible material.

Edit guide specification to include only information specific to your project.  Delete or add text, select appropriate bracketed phrases, and fill in blanks as required. Go to Berner catalog or website (www.berner.com) to select specific models and sizes that are required for project and to obtain data necessary to edit this specification section.

Coordinate specification with information shown on project drawings and schedules. In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules. Cross check mechanical and architectural drawings.

This guide specification is available in word processing format at www.berner.com.  Turn on “Hidden Text” function in your word processor to display “Specifier Notes.”

For additional information or name of Berner representative in your area, call Berner International Corporation at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.berner.com. A selection guide is available at www.berner.com to suggest models appropriate for typical applications.

- GENERAL

      - CONDITIONS AND REQUIREMENTS

        - The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

      - SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

        - Air curtains[, electric heated] [, hot water heated] [, steam heated] [, positive indirect gas heated] [, direct gas heated].

        - [Insert item description.]

      - RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

        - Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

        - Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

        - Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note: If switches for air curtains are mounted on door frames, retain either Section 08 11 00 or 08 41 00 below to facilitate coordination.

        - Section 08 11 00 - Metal Doors and Frames:  Coordinate installation of switches.

Specifier Note:  Strip doors can be used in conjunction with air curtains to provide an even higher level of separation.  Retain first paragraph below if required for a specific project.  Consult Berner catalog for a complete list of available strip doors.

        - Section 08 38 13 - Flexible Strip Doors:  Coordinate installation of strip doors with installation of air curtains.

        - Section 08 41 00 - Entrances and Storefronts:  Coordinate installation of switches.

- Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air curtain must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

        - Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware.

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to field painted.  Protect electrical contacts and moveable parts from paint.

        - Section 09 91 00 - Painting:  Field applied finishes.

Specifier Note:  Retain the following paragraph if hot water heaters are used in air curtains.

        - Division 22 - Plumbing:  Connection of hot water supply to heater used in air curtains.

Specifier Note:  Retain the following paragraph if steam or gas heaters are used in air curtains.

        - Division 23 - Heating, Ventilating, and Air-Conditioning (HVAC):  Connection of steam or gas supply to heater used in air curtains.

        - Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

        - Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

      - REFERENCE STANDARDS

Specifier Note:  Retain the following paragraph and subparagraph if steam or hot water heated units are required for a specific project.

        - Air Conditioning & Refrigeration Institute (ARI):

          - ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

        - Canadian Standards Association (CSA):

          - ANSI Z83.8-2013/CSA 2.6-2013 - Gas unit heaters, gas packaged heaters, gas utility heaters and gas-fired duct furnaces.

        - Air Movement & Control Association International, Inc. (AMCA):

          - AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.

          - AMCA 220 - Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings.

          - AMCA 222 - Application Manual for Air Curtain Units.

        - National Electrical Manufacturers Association (NEMA):

          - NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

Specifier Note:  Retain the following paragraph and subparagraph if direct or indirect gas heated units are required on a specific project.

        - National Fire Protection Association (NFPA):

          - NFPA 54 - National Fuel Gas Code.

        - Underwriters Laboratories (UL):

          - UL 507 - Electric Fans.

          - UL 508 - Industrial Control Equipment.

      - SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

        - Submit under provisions of Section [01 33 00] [______].

        - Product Data:  Submit for [____________] including:

          - [_____________________.]

          - Rated capacities.

          - Operating characteristics.

          - Accessories.

          - Options.

Specifier Note:  Retain the last sentence in the following paragraph if specifying electric heated models in section.

        - Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

          - Indicate dimensions, weights, loads, clearances required, location and size of field connections.

          - Provide wiring diagrams for power, signal, and control wiring.

        - Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

        - Warranties:  Sample of special warranties.

      - QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

        - Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

        - Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Specifier Note:  Retain the following paragraph if specifying the ambient type of air curtain in this section.

        - Comply with AMCA 211, for airflow rate, average outlet velocity, outlet velocity uniformity, velocity projection and power rating.

        - Certification:

Specifier Note:  Retain either of the following two subparagraphs to agree with type of unit selected for a project and delete the other.  Retain both subparagraphs if project has both types of units.

          - Unheated Units:  Test units in accordance with AMCA 220.  Provide units with AMCA Certified Ratings Seal.

          - Heated Units:  Test units in accordance with AMCA 220 except for inclusion of heating.

- Specifier Note:  Retain the following paragraph if specifying the steam or hot water type of air curtain in this section.

        - Comply with ARI 410 for components, construction, and rating.

          - Certify coils in accordance with ARI 410.

- Specifier Note:  Retain the following paragraph if specifying the indirect gas heated type of air curtain in this section.

        - Indirect gas fired unit heaters to be CSA listed for construction and rating.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver air curtains in factory labeled packages.

        - Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

        - Protect from damage due to weather, excessive temperature, and construction operations.

      - WARRANTY

        - Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

Specifier Note:  Retain either of the following two subparagraphs to agree with type of unit selected for a project and delete the other. Retain both subparagraphs if project has both types of units.

          - Five-year limited warranty for unheated units.

          - Two-year limited warranty for heated units.

- PRODUCTS

      - MANUFACTURERS

        - Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International Corporation, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

        - Substitutions are not permitted.

        - Substitutions will be considered under provisions of Section 01 60 00.

      - AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are not required.

        - Acceptable Products:  Berner Industrial [Direct Drive 16 Model [IDC16 Ambient] [IDC16 Electric Heated] [IDC16 Hot Water Heated] [IDC16 Steam Heated] [IDC16 Positive Indirect Gas Heated] [IDC16 Direct Gas Heated]] [and] [Belt Drive 16 [IBC16 Ambient] [IBC16 Hot Water Heated] [IBC16 Steam Heated] [IBC16 Positive Indirect Gas Heated] [IBC16 Direct Gas Heated]].

        - Construction:  Provide factory-assembled units of sufficient structural strength to be supported from ends without intermediate support.  Ship units completely assembled.  Units shall have split cabinet with removable lower section for access to internal components.

        - Cabinet:

- Specifier Note: Retain one of the options in the following subparagraph. Standard cabinet construction is welded aluminized steel with powder coated gray finish; optional cabinet in stainless steel or custom color powder coated aluminized steel.

          - Material and Finish:  Minimum 14-gage [aluminized steel with [gray] [insert color selection] powder coated finish] [stainless steel] welded construction.

          - Dimensions: Air curtain cabinet (not including external heating options) not to exceed 21 in (53.3 cm) high by 32.25 in (81.9 cm) deep.

          - Mounting:  Provide for [wall] [suspension] [vertical] mounting.  [Provide for tandem mounting for vertical position only.]

- Specifier Note: Retain one of the options in the following subparagraph if desired as an option for Direct Drive models or standard construction for Belt Drive models. Standard location for Direct drive is opposite intake location (i.e. front intake requires top access panels). Standard location for Belt Drive models is same as motor location (i.e. front mounted motor requires front access panels). Standard material is mill finish aluminized steel; optional material is stainless steel.

          - Service Access: Removable lower blower section [with [top] [front] access panels] constructed from [mill finish aluminized] [stainless] steel.

        - Motors:  Number and horsepower of motors shall be as scheduled.

Specifier Note:  Retain the first subparagraph below if specifying Model Industrial Direct Drive 16 (IDC16); retain the second subparagraph below and select motor location if specifying Model Industrial Belt Drive 16 (IBC16); standard location is top-right hand mount.

          - [Direct Drive:  1160 RPM, three phase, 1-speed, totally enclosed air over (TEAO), foot mounted, continuous duty, requiring external thermal overload protection with re-greaseable ball bearings.]

          - [Belt Drive:  1750 RPM, three phase, 1-speed, totally enclosed fan cooled (TEFC), foot mounted, continuous duty, requiring external thermal overload protection with re-greaseable ball bearings; locate motors outside air stream. Mounted on the [top-right] [top-left] [front-right] [front-left] hand side of cabinet.]

        - Fans:  Balanced forward curved centrifugal type, double inlet, double width design with welded hubs, mounted in matched fan housings with aerodynamically formed air inlet venturis.  Manufacture wheels and housings from galvanized steel.

          - Drive blower wheels through flexible couplings.  Support each blower wheel by two (2) permanently lubricated one (1) inch (25.4 mm) sealed ball bearings encased in vibration isolating rubber cartridges.

        - Discharge Nozzles:

          - Provide uniform velocity across width of air curtain.

          - Mount on continuous piano hinge to allow deflection of air stream ± 20 degrees without loss of discharge velocity or opening area.

          - Aperture:  4.5 in (11.4 cm) by width of air curtain.

          - Vane: 3.5 inches (8.9 cm) minimum height; constructed of airfoil-shaped aluminum extrusions.

          - Includes air volume control damper constructed of same material as cabinet.

        - Inlet:

Specifier Note:  Top air intake in the following subparagraph only available on unheated, steam/hot water heated, and direct gas fired units.

          - Location: [Front] [Top].

          - Screen:  Expanded metal with welded frame constructed of same material used in cabinet.

Specifier Note:  In the following paragraph, flat-faced filter rack is not available for disposable or polyester media.

        - Air Inlet Filter:  [Flat-faced] [V-bank] type, [re-cleanable aluminum] [disposable] [re-cleanable polyester with aluminum frame] with hinged inlet screen.

Specifier Note:  Retain the following article if heated units are required for a specific project.

      - HEATING ELEMENTS

        - Electric Heating Coil:  UL-approved construction, factory-mounted, factory-wired, thermally-protected, galvanized steel frame.

          - Duct mount helical coil with barrel or point supported elements wired in a three phase circuit. Automatic and manual reset limit controls, primary magnetic contactors, equipment grounding lug, power fusing, and control transformer.

        - Steam Coil: Certified in accordance with ARI 410; constructed from 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins.

          - Characteristics:  Design to operate at maximum 150-psig (1035-kPa) and 366 degrees F (185 degrees C) steam.

          - Leak-test under water at 450-psig (3103-kPa) dry nitrogen.

          - Factory mount coil on air intake and protect with expanded metal screen.

        - Hot Water Coil:  Certified in accordance with ARI 410; constructed from 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins.

          - Characteristics:  Design to operate at maximum 250-psig (1720-kPa) and 300 degrees F (149 degrees C) hot water.

          - Leak-test under water at 450-psig (3103-kPa) dry nitrogen.

          - Factory mount coil on air intake and protect with expanded metal screen.

        - Indirect Gas Heater and Duct Transition:

          - CSA Listed.

          - Fuel Type:  Provide orifices for [natural gas] [LP gas].

          - Heat Exchanger and Burner:  [Aluminized] [Stainless] steel.

          - Characteristics:  120-volt [separate] [single point] supply voltage, power exhaust vent, 120-volt limit control, 24-volt control voltage transformer, combustion air pressure switch, spark ignited intermittent safety pilot system with electronic flame supervision.

          - Independently support each heater at least one (1) inch (25 mm) from each opening of factory-installed duct transition.  Construct duct transition from 16-gage aluminized steel with access panels spanning entire width.

        - Direct Gas Fired Heater:

          - Fuel Type:  Provide orifices for natural gas.

          - Characteristics:  Provide minimum turndown ratio of 30:1 stainless steel baffles, non-clogging orifices, ignition system, flame safeguard, gas manifold, valves, and temperature controls.

          - Gas Manifold (Train):  As required by [ANSI] [and] [FM] [and] [industrial risk insurance (IRI)].

          - Spark ignited intermittent pilot.

      - CONTROLS

        - Control Panel:

- Specifier Note: In the following subparagraph 120V control voltage is standard, 24V is optional.

          - UL listed, industrial type, pre-wired, with components consisting of motor starter, terminal strip, motor overloads, and control transformer with [120] [24] volt fused secondary.

Specifier Note: Single power supply is standard on unheated and hot water/steam heated units.  Electric heated units have single or multiple power supplies based on voltage and kW rating.  Indirect gas heated units have standard multiple power supplies (one per air curtain and one for each heater), single point power supply is available.

          - [Multiple] [Single] power supply.

Specifier Note:  Retain the Type 4X enclosure in areas subject to corrosive or wash-down type conditions and delete the first option.

          - Enclosure:  Oil-tight and dust-tight NEMA Type [4/12] [corrosion resistant NEMA 4X [polycarbonate] [stainless steel]] enclosure with neoprene door gasket.

- Specifier Note: Select the location of the control panel. Remote mounted control panels are standard on all units.  Optional unit mounted control panel available for direct drive (IDC16), unit mounting for belt drive (IBC16) only available opposite-hand side of the motor location.

          - Mounting:  [Remote mounted as indicated on Drawings.] [Unit mounted [right end] [left end].]

Specifier Note:  Retain the following paragraph if a disconnect switch is required to simplify power shut-off when servicing air curtain.  Delete the following subparagraph if this option is not selected for a specific project.

          - Disconnect Switch:  Provide lockable panel mounted through the door rotary [fused] [non-fused] disconnect.

Specifier Note:  Time delay relay is standard for units with gas heaters and recommended for doors which have frequent opening and closing cycles.  The air curtain turns on when door is opened and shuts off after the door is closed and the set delay time expires.  Delete the following subparagraph if this option is not selected for a specific project.

          - Time Delay Relay:  Adjustable from 0.1 second to 10 hour delay.  Set delay for [one (1)] [insert time in minutes] minute(s).

Specifier Note:  Retain one of the three following subparagraphs if an activation device is required in the panel on a project. Remote mounted is standard, factory installed is optional. START-STOP not available in conjunction with door switch or time delay.

          - Switching:

            - [HAND-OFF-AUTOMATIC Switch:  Panel mounted switch allows manual on-off operation or operation controlled by automatic door switch that activates unit when door opens and deactivates unit when door closes.]

            - [START-STOP Switch:  Panel mounted switch for manual start-stop push button operation.]

            - [ON-OFF Switch:  Panel mounted switch for manual on-off operation.]

Specifier Note:  Retain the following subparagraph to lockout heat on electric or gas heated units.

            - [[HEAT ON-OFF] [SUMMER-WINTER] Switch:  Panel mounted switch to manually lock out heat operation.]

Specifier Note:  Retain the following paragraph for indirect gas fired heated units requiring single point power supply.  Remote mounting is standard, unit mounted is available.  Delete the following subparagraph if this option is not selected for a specific project.

        - [Remote] [Unit] mounted Dry-type distribution transformer.

        - Remote Activation Devices:

          - [Automatic Door Switch:  Switch automatically activates unit when door opens and deactivates unit when door closes.]

          - [HAND-OFF-AUTOMATIC Switch:  Switch allows manual on-off operation or operation controlled by automatic door switch that activates unit when door opens and deactivates unit when door closes.]

- Specifier Note:  START-STOP switch is not available in conjunction with either the door switch or time delay option.

          - [START-STOP Switch:  Provides manual start-stop push button operation.]

          - [ON-OFF Switch:  Allows manual on-off operation.]

Specifier Note:  Retain the following subparagraph to lockout heat on electric or gas heated units.

          - [[HEAT-ON-OFF] [SUMMER-WINTER] Provides manual lock out for heat operation.]

Specifier Note:  Retain the following paragraph when specifying electric or gas heated units.  Delete the following subparagraph if this option is not selected for a specific project.

        - Thermostat:  Prevents operation of heater when inside air temperature exceeds desired temperature.

Specifier Note:  Retain the following paragraph to coordinate operational sequence of air curtain controls.

        - Sequencing:  [___________________________________________________.]

      - MOUNTING ACCESSORIES

Specifier Note:  Show mounting brackets on Drawings if required.

        - Provide brackets and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

Specifier Note:  Retain the applicable brackets from the list below and delete those not required for a project. Standard wall bracket material is 2 in (5.1 cm) x 4 in (10.2 cm) tube constructed from mild carbon steel with gray powder coated finish; optional in stainless steel or custom color powder coated mild carbon steel.

          - Wall Brackets:  [0 in (0 cm)] [6 in (15.2 cm)] [8 in (20.3 cm)] [10 in (25.4 cm)] [12 in (30.5 cm)] [14 in (35.6 cm)] [16 in (40.6 cm)] [18 in (45.7 cm)] constructed from 2 in (5.1 cm) x 4 in (10.2 cm) [mild carbon steel tubing with [gray] [insert color selection] powder coated finish] [stainless steel tubing].

- Specifier Note:  Retain the following paragraph only if vertical mounting air curtain.  Standard floor bracket material is mild carbon steel with gray powder coated finish; optional in stainless steel or custom color powder coated mild carbon steel

          - Floor Brackets:  For vertical installation only - maximum 30 ft (914.4 cm) tall; manufactured from [mild carbon steel with [gray] [insert color selection] powder coated finish] [stainless steel].

Specifier Note:  Extension brackets are not available on units where the control panel is factory-mounted on the end of unit. Standard bracket material is aluminized steel with gray powder coated finish; optional in stainless steel or custom color powder coated aluminized steel.

          - Extension Brackets:  [6 in (15.2)] [12 in (30.5 cm)] mounted on [right hand] [left hand] [both] end plate(s).

- Specifier Note:  Retain the following paragraph only if vertical mounting air curtain.  Standard tandem bracket material is mild carbon steel with gray powder coated finish; optional in stainless steel or custom color powder coated mild carbon steel.

          - Tandem Brackets:  For between vertical mounted units only - maximum 30 ft (914.4 cm) tall; manufactured from [mild carbon steel with [gray] [insert color selection] powder coated finish] [stainless steel].

- EXECUTION

      - EXAMINATION

        - Verify that door frame and adjacent construction are installed correctly and are ready to receive work of this Section.

        - Verify that utilities are in correct location and are of correct capacities for specified products.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

        - Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

        - Securely install air curtains plumb, level, and as close as practical to top of opening and face of wall.

        - Install switches where indicated on Drawings.

      - CONNECTIONS

Specifier Note:  Retain the appropriate option in the following paragraph depending on type of air curtain(s) retained in Part 2 - Products and delete those not used.

        - Connect air curtain to utilities as specified in [Division 22] [Division 23] [Division 26] sections.

      - FIELD QUALITY CONTROL

        - Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

        - Test and operate air curtain to be sure that it performs as intended.

      - ADJUSTING

        - Adjust fan speed to prepare installed products to perform properly.

      - CLEANING

        - Clean air curtain prior to commissioning.

        - Repair or repaint damage to finishes on exposed-to-view surfaces.

      - SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

        - Test and operate air curtains to ensure that they perform as intended.  Adjust discharge nozzles to deflect air outward [unless otherwise required].

      - DEMONSTRATION

        - Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2014 Berner International Corporation.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Revised 04/14