SECTION 23 34 33

AIR CURTAINS

### Berner Series Industrial Direct Drive 14 (IDC14) air curtains (a.k.a. air doors) are designed for industrial applications such as service or dock doors. They are suitable for opening heights up to 14 ft (426.7 cm) for environmental separation and up to 12 ft (365.8 cm) for insect control.

### Air curtains provide environmental separation at openings by reducing the infiltration of unconditioned air, fumes, dust, and humidity.  At exterior openings, they can resist winds up to 10 MPH (16 KPH) and are generally mounted inside the building. During cold seasons warm air that has risen towards ceiling is recirculated; they can also be used at interior openings such as doors to coolers or clean rooms.  Optimum protection is provided when units are mounted flush to the wall and as close to top of door opening as possible.   To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

### Series IDC14 model air curtains have 1 HP motors.  They can be wall mounted or suspended from the ceiling.  Electric heated units shall be installed indoors only and require – a minimum clearance of at least 6 ft (182.9 cm) between the bottom of the unit and the floor, a minimum of 8 in (20.3 cm) between the top and ceiling and 1 in (2.5 cm) between the sides and any combustible material.

### Edit guide specification to include only information specific to your project.  Delete or add text, select appropriate bracketed phrases, and fill in blanks as required.  Go to Berner catalog or website (www.berner.com) to select specific models and sizes that are required for project and to obtain data necessary to edit this specification section.

### Coordinate specification with information shown on project drawings and schedules.  In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules.  Cross check mechanical and architectural drawings.

### This guide specification is available in word processing format at www.berner.com.  Turn on “Hidden Text” function in your word processor to display “Specifier Notes.”

For additional information or name of Berner representative in your area, call Berner International Corporation at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.berner.com. A selection guide is available at www.berner.com to suggest models appropriate for typical applications.

- GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

Air curtains[, electric heated] [, hot water heated] [, steam heated] [, positive indirect gas heated].

[Insert item description.]

RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note: If switches for air curtains are mounted on door frames, retain either Section 08 11 00 or 08 41 00 below to facilitate coordination.

Section 08 11 00 - Metal Doors and Frames:  Coordinate installation of switches.

Specifier Note:  Strip doors can be used in conjunction with air curtains to provide an even higher level of separation.  Retain first paragraph below if required for a specific project.  Consult Berner catalog for a complete list of available strip doors.

Section 08 38 13 - Flexible Strip Doors:  Coordinate installation of strip doors with installation of air curtains.

Section 08 41 00 - Entrances and Storefronts:  Coordinate installation of switches.

Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air door must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware.

Specifier Note:  Retain any of the three following paragraphs if air curtains are mounted above ceiling.  Delete if no units installed above ceiling.

Section 09 22 16 - Non-Structural Metal Framing:  Framing and blocking above ceiling as required for installation of air curtain.

Section 09 29 00 - Gypsum Board:  Ceiling finish abutting air curtain.

Section 09 51 13 - Acoustical Panel Ceilings:  Ceiling finish abutting air curtain.

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to be field painted.  Protect electrical contacts and moveable parts from paint.

Section 09 91 00 - Painting:  Field applied finishes.

Specifier Note:  Retain the following paragraph if hot water heaters are used in air curtains.

Division 22 - Plumbing:  Connection of hot water supply to heater used in air curtains.

Specifier Note:  Retain the following paragraph if steam or gas heaters are used in air curtains.

Division 23 - Heating, Ventilating, and Air-Conditioning (HVAC):  Connection of steam or gas supply to heater used in air curtains.

Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

REFERENCE STANDARDS

Specifier Note:  Retain the following paragraph and subparagraph if steam or hot water heated units are required for a specific project.

Air Conditioning & Refrigeration Institute (ARI):

ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

Specifier Note:  Retain the following paragraph and subparagraph if indirect gas heated units are required for a specific project.

Canadian Standards Association (CSA):

ANSI Z83.8-2013/CSA 2.6-2013 - Gas unit heaters, gas packaged heaters, gas utility heaters and gas-fired duct furnaces.

Air Movement & Control Association International, Inc. (AMCA):

AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.

AMCA 220 - Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings.

AMCA 222 - Application Manual for Air Curtain Units.

National Electrical Manufacturers Association (NEMA):

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

Specifier Note:  Retain the following paragraph and subparagraph if indirect gas heated units are required on a specific project.

National Fire Protection Association (NFPA):

NFPA 54 - National Fuel Gas Code.

Underwriters Laboratories (UL):

UL 507 - Electric Fans.

UL 508 - Industrial Control Equipment.

UL 2021 - Fixed and Location-Dedicated Electric Room Heaters.

UL 1995 - Heating and Cooling Equipment

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for [____________] including:

[_____________________.]

Rated capacities.

Operating characteristics.

Accessories.

Options.

Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

          - Indicate dimensions, weights, loads, clearances required, location and size of field connections.

Provide wiring diagrams for power, signal, and control wiring.

Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

Warranties:  Sample of special warranties.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Specifier Note:  Retain the following paragraph if specifying the ambient type of air curtain in this section.

Comply with AMCA 211, for airflow rate, average outlet velocity, outlet velocity uniformity, velocity projection and power rating.

Certification:

Specifier Note:  Retain either of the first two subparagraphs to agree with type of unit selected for a project and delete the other.  Retain both subparagraphs if project has both types of units.

Unheated Units:  Test units in accordance with AMCA 220.  Provide units with AMCA Certified Ratings Seal.

Heated Units:  Test units in accordance with AMCA 220 except for inclusion of heating.

Unheated and electric heated units to be UL Listed in the United States and Canada.

Specifier Note:  Retain the following paragraph if specifying the steam or hot water type of air curtain in this section.

Comply with ARI 410 for components, construction, and rating.

Certify coils in accordance with ARI 410.

Specifier Note:  Retain the following paragraph if specifying the indirect gas heated type of air curtain in this section.

Indirect gas fired unit heaters to be CSA listed for construction and rating.

DELIVERY, STORAGE AND HANDLING

Deliver air curtains in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

WARRANTY

Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

Specifier Note:  Retain either of the following two subparagraphs to agree with type of unit selected for a project and delete the other. Retain both subparagraphs if project has both types of units.

Five-year limited warranty for unheated units.

Two-year limited warranty for heated units.

- PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International Corporation, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

Substitutions are not permitted.

Substitutions will be considered under provisions of Section 01 60 00.

AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are required.

Acceptable Products:  Berner Industrial Direct Drive 14 Model [IDC14 Ambient] [IDC14 Electric Heated] [IDC14 Hot Water Heated] [IDC14 Steam Heated] [IDC14 Positive Indirect Gas Heated].

Construction:  Provide factory-assembled units of sufficient structural strength to be supported from ends without intermediate support.  Ship units completely assembled.

Cabinet:

Specifier Note: Retain one of the options in the following subparagraph. Standard cabinet construction is welded aluminized steel with powder coated gray finish; optional cabinet in stainless steel or custom color powder coated aluminized steel.

Material and Finish:  Minimum 16-gage [aluminized steel with [gray] [insert color selection] powder coated finish base frame with mill aluminum inlet screen and access panels] [stainless steel base frame, access panels and screen] welded construction.  [Tamper-resistant construction; parts cannot be disassembled without special tool provided by manufacturer.]

Dimensions: Air curtain cabinet (not including external heating options) not to exceed 15 in (38.1 cm) high by 18 in (45.7 cm) deep.

Specifier Note:  Retain only the mounting method required for a specific project in the following subparagraph and delete the others.

Mounting:  Provide for [wall] [suspension] [vertical] mounting.  [Provide for tandem mounting for vertical position only.]

Service Access: Removable screen, top and bottom access panels.

Specifier Note: Retain the motor type that is required and delete the others. Standard construction uses 1-HP, ODP, 1-speed, single phase motor for ALL single and three phase power supplies, optional ODP, 2-speed, single phase motor for ALL single and three phase power supplies TEAO, 1-speed, three phase motor for three phase power supplies or TEAO, 2-speed, three phase motor for three phase power supplies available.

Motors:  1-HP, 1680 RPM, [single phase, [1] [3]-speed, ODP, direct drive, resilient mounted, continuous duty, with internal thermal-overload protection and permanently lubricated sealed ball bearings for single and three phase power supplies] [three phase, [1] [2] speed, TEAO, direct drive, resilient mounted, continuous duty, requiring external thermal-overload protection with permanently lubricated sealed ball bearings for three phase power supply].

Fans:  Balanced forward curved centrifugal type, double inlet, mounted in matched fan housings with aerodynamically formed air inlet venturis.  Manufacture wheels and housings from galvanized steel.

Discharge Nozzles:

Provide uniform velocity across width of air curtain.

Aperture:  3.5 in (9 cm) slot by width of air curtain.

Vanes: 1.5 in (3.8 cm) minimum height; constructed of airfoil-shaped aluminum extrusions; adjustable plus or minus 20 degrees to deflect airflow.

Specifier Note:  Retain the following paragraph for all unheated and heated units installed above the ceiling.  Extensions are either provided constructed from 21 in (53.3 cm) high aluminized steel suitable for field cutting to length or fixed 6 in (15.2 cm) high clear anodized aluminum.  Standard air directional vanes are aluminum, while white aluminum multi-blade air discharge grilles are optional.

Nozzle Extension:  [Unpainted aluminized steel] [Clear anodized aluminum] with airfoil shaped [1.5 in (3.8 cm) aluminum discharge vanes] [0.875 in (2.2 cm) white aluminum multi-blade air discharge grille].

Inlet:

Location: [Front] [Top].

Specifier Note:  Retain the option that is required after editing the material and finish type in Paragraph 2.2C above and delete the others.

Screen:  Perforated pattern [mill aluminum] [stainless steel] with border.

Specifier Note:  Retain the following paragraph optional filters are required for a specific project. Select desired filter type and delete the others.

Air Inlet Filter:  [Flat-faced re-cleanable aluminum] [Flat-faced re-cleanable polyester with aluminum frame] [with screen] [without screen].

Specifier Note:  Retain the following article if heated units are required for a specific project.

HEATING ELEMENTS

Electric Heating Coil:  UL-approved, factory-mounted, factory-wired, thermally-protected, galvanized steel frame.

Venturi mounted helical coil with point suspended elements, [single] [three] phase circuit.

Thermal Cutout: Locks out electric heaters when prolonged abnormal over-temperature conditions exist.

Steam Coil: Certified in accordance with ARI 410; constructed from 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins.

Characteristics:  Design to operate at maximum 150-psig (1035-kPa) and 366 degrees F (185 degrees C) steam.

Leak-test under water at 350-psig (2410-kPa) dry nitrogen.

Factory mount coil on air intake and protect with perforated metal screen.

Hot Water Coil:  Certified in accordance with ARI 410; constructed from 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins.

Characteristics:  Design to operate at maximum 250-psig (1720-kPa) and 300 degrees F (149 degrees C) hot water.

Leak-test under water at 350-psig (2410-kPa) dry nitrogen.

Factory mount coil on air intake and protect with perforated metal screen.

Indirect Gas Heater and Duct Transition:

CSA listed.

Fuel Type:  Provide orifices for [natural gas] [LP gas].

Heat Exchanger and Burner:  [Aluminum] [Stainless steel].

Characteristics:  120-volt [separate] [single point] supply voltage, power exhaust vent, 120-volt limit control, 24-volt control voltage transformer, combustion air pressure switch, spark ignited intermittent safety pilot system with electronic flame supervision.

Independently support each heater at least one (1) inch (25 mm) from each opening of factory-installed duct transition.  Construct duct transition from 16-gage aluminized steel with access panels spanning entire width.

CONTROLS

Control Panel:

Specifier Note: In the following subparagraph 120V control voltage is standard, 24V is optional except for electric heated units where 24V is standard.  Motor overloads are only available for three phase motors.

UL listed, industrial type, pre-wired, with components consisting of motor starter, terminal strip, [motor overloads], and control transformer with [120] [24] volt fused secondary.

Specifier Note: Single power supply is standard on unheated and hot water/steam heated units.  Electric heated units have single or multiple power supplies based on voltage and kW rating.  Indirect gas heated units have standard multiple power supplies (one per air curtain and one for each heater), single point power supply is available.

[Multiple] [Single] power supply.

Specifier Note:  Retain the Type 4X enclosure in areas subject to corrosive or wash-down type conditions and delete the first option.

Enclosure:  Oil-tight and dust-tight NEMA Type [4/12] [corrosion resistant NEMA 4X [polycarbonate] [stainless steel]] enclosure with neoprene door gasket.

Specifier Note: Select the location of the control panel. Unit mounted control panels are standard on all units, remote mounting is optional.

Mounting:  [Remote mounted as indicated on Drawings.] [Unit mounted [right end] [left end].]

Specifier Note:  Retain the following paragraph if a disconnect switch is required to simplify power shut-off when servicing air curtain.  Delete the following subparagraph if this option is not selected for a specific project. Panel mounted rotary disconnect only available for control panels with a single circuit.

Disconnect Switch:  Provide lockable [[remote] [unit] mounted non-fused toggle disconnects based on number of power supplies required] [panel mounted through the door rotary [fused] [non-fused] disconnect].

Specifier Note: For electric heated units refer to paragraph 2.4D for Control Packages specifically designed for electric heated sequences. For all other units continue with the following paragraphs for individual component selection.

Specifier Note:  Time delay relay is standard for units with gas heaters and recommended for doors which have frequent opening and closing cycles.  The air curtain turns on when door is opened and shuts off after the door is closed and the set delay time expires.  Delete the following subparagraph if this option is not selected for a specific project.

Time Delay Relay:  Adjustable from 0.1 second to 10 hour delay.  Set delay for [one (1)] [insert time in minutes] minute(s).

Specifier Note:  Retain one of the three following subparagraphs if an activation device is required in the panel on a project. Remote mounted is standard, factory installed is optional. START-STOP not available in conjunction with door switch or time delay.

Switching:

[HAND-OFF-AUTOMATIC Switch:  Panel mounted switch allows manual on-off operation or operation controlled by automatic door switch that activates unit when door opens and deactivates unit when door closes.]

[START-STOP Switch:  Panel mounted switch for manual start-stop push button operation.]

[ON-OFF Switch:  Panel mounted switch for manual on-off operation.]

Specifier Note:  Retain the following subparagraph to lockout heat on electric or gas heated units.

[[HEAT ON-OFF] [SUMMER-WINTER] Switch:  Panel mounted switch to manually lock out heat operation.]

Specifier Note:  Retain the following paragraph for indirect gas fired heated units requiring single point power supply.  Remote mounting is standard, unit mounted is available.  Delete the following subparagraph if this option is not selected for a specific project.

[Remote] [Unit] mounted Dry-type distribution transformer.

Remote Activation Devices:

[Automatic Door Switch:  Switch automatically activates unit when door opens and deactivates unit when door closes.]

[HAND-OFF-AUTOMATIC Switch:  Switch allows manual on-off operation or operation controlled by automatic door switch that activates unit when door opens and deactivates unit when door closes.]

Specifier Note:  START-STOP switch is not available in conjunction with either the door switch or time delay option.

[START-STOP Switch:  Provides manual start-stop push button operation.]

[ON-OFF Switch:  Provides manual on-off operation.]

Specifier Note:  Retain the following subparagraph to lockout heat on electric or gas heated units.

[[HEAT ON-OFF] [SUMMER-WINTER] Switch:  Provides manual lock out for heat operation.]

Specifier Note:  For electric heated units only, retain one of the following three paragraphs and delete the other two.  In the first paragraph the air curtain turns on when door is opened and shuts off when door is closed.  This package can only be used on electric heated models.

Control Packages:

Basic 24V Control Package:  Air curtain turns on when door is opened and shuts off when door is closed.

Specifier Note:  Retain only one of the three options in the following subparagraph and delete the other two.  If retaining the first option select either NEMA 1 or 4 and delete the other one.

24 Volt Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] [Magnetic reed] style door switch.

Specifier Note:  In the following paragraph the air curtain turns on when door is opened and shuts off after the door is closed and the set delay time expires.  This package can only be used on electric heated models.

Deluxe 24V Control Package:  Air curtain turns on when door is opened and shuts off when door is closed, unit remains on until set delay time expires.

Specifier Note:  Retain only one of the three options in the following subparagraph and delete the other two.  If retaining the first option select either NEMA 1 or 4 and delete the other one.

24 Volt Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] [Magnetic reed] style door switch and factory-installed time delay.

Specifier Note:  Retain the following paragraph only if three speed electric heated units are required for a specific project.

Comfort Plus 24 Volt Control Package:  Provides supplemental heat when door is closed and allows the air curtain to run at the speed selected to protect the opening when the door is opened.  The air curtain shuts off after the door is closed and the set delay time expires. When the door is closed and the temperature drops below the set point the air curtain runs at low speed providing supplemental heat until the thermostat is satisfied.

Provide package complete with [magnetic reed] [NEMA [1] [4] plunger] [NEMA 1 roller arm] style door switch, factory-installed transformer, time delay and thermostat.

Specifier Note:  Retain the following paragraph when specifying electric or gas heated units.  Delete the following subparagraph if this option is not selected for a specific project.

Thermostat:  Prevents operation of heater when inside air temperature exceeds desired temperature.

Specifier Note:  Retain the following paragraph and insert text describing coordinating operational sequence of air curtain controls if required.

Sequencing:  [______________________________.]

MOUNTING ACCESSORIES

Specifier Note:  Show mounting brackets on Drawings if required.

Provide brackets and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

Specifier Note:  Retain the applicable brackets from the list below and delete those not required for a project. Standard wall bracket material is galvanized steel with gray powder coated finish; optional in stainless steel or custom color powder coated galvanized steel.

Wall Brackets:  [0-12 in (0-30.5 cm)] [0-20 in (50.8 cm)] from [[galvanized steel with [gray] [insert color selection] powder coated finish] [stainless steel] structural channel.

Specifier Note:  Retain the following paragraph only if vertical mounting air curtain.  Standard floor bracket material is mild carbon steel with gray powder coated finish; optional in stainless steel or custom color powder coated mild carbon steel.

Floor Brackets:  For vertical installation only - maximum 30 ft (914.4 cm) tall; manufactured from [mild carbon steel with [gray] [insert color selection] powder coated finish] [stainless steel].

Specifier Note:  Extension brackets are not available on units where the control panel is factory-mounted on the end of unit. Standard bracket material is aluminized steel with gray powder coated finish; optional in stainless steel or custom color powder coated aluminized steel.

Extension Brackets:  [6 in (15.2)] [12 in (30.5 cm)] mounted on [right hand] [left hand] [both] end plate(s).

Specifier Note:  Retain the following paragraph only if vertical mounting air curtain.  Standard tandem bracket material is mild carbon steel with gray powder coated finish; optional in stainless steel or custom color powder coated mild carbon steel.

Tandem Brackets:  For between vertical mounted units only - maximum 30 ft (914.4 cm) tall; manufactured from [mild carbon steel with [gray] [insert color selection] powder coated finish] [stainless steel].

- EXECUTION

EXAMINATION

Verify that door frame and adjacent construction are installed correctly and are ready to receive work of this Section.

Verify that utilities are in correct location and are of correct capacities for specified products.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

Securely install air curtains plumb, level, and as close as practical to top of opening and face of wall.

Install switches where indicated on Drawings.

CONNECTIONS

Specifier Note:  Retain the appropriate option in the following paragraph depending on type of air curtain(s) retained in Part 2 - Products and delete those not used.

Connect air curtain to utilities as specified in [Division 22] [Division 23] [Division 26] sections.

FIELD QUALITY CONTROL

Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Test and operate air curtain to be sure that it performs as intended.

ADJUSTING

Adjust fan speed to prepare installed products to perform properly.

Specifier Note: Delete the optional text in the following paragraph if not required for a specific project.

Adjust discharge nozzles to deflect air outward [unless otherwise required].

CLEANING

Clean air curtain prior to commissioning.

Repair or repaint damage to finishes on exposed-to-view surfaces.

SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

Test and operate air curtains to ensure that they perform as intended.  Adjust discharge nozzles to deflect air outward [unless otherwise required].

DEMONSTRATION

Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2014 Berner International Corporation.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Revised 04/14