SECTION 23 34 33

AIR CURTAINS

Berner Sanitation Certified Low Profile 7 Series (SLC07) air curtains (a.k.a. air doors) are designed to be mounted inside or outside on exterior doors customer entry and service entry doors with low ceiling clearance or pass thru windows. They meet the requirements of ANSI/NSF Standard 37 for opening heights up to 7 ft (213.4 cm) high for insect control.

Optimum protection is provided when units are mounted flush to the wall and as close to top of door opening as possible.   To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

Series SLC07 model air curtains have 1/5 HP motors. They can be wall mounted or suspended from the ceiling.

Edit guide specification to include only information specific to your project. Delete or add text, select appropriate bracketed phrases, and fill in blanks as required. Go to Berner catalog or website to select specific models and sizes that are required for project and to obtain data necessary to edit this document.

Coordinate specification with information shown on project drawings and schedules. In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules. Cross check mechanical and architectural drawings.

This guide specification is available in word processing format at www.berner.com.  Turn on “Hidden Text” function in your word processor to display “Specifier Notes.”

For additional information or name of Berner representative in your area, call Berner International Corporation at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.Berner.com. A selection guide is available at www.Berner.com to suggest models appropriate for typical applications.

- GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

Air curtains.

[Insert item description.]

RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note:  If switches for air curtains are mounted on door frames, retain either Section 08 11 00 or 08 41 00 below to facilitate coordination.

Section 08 11 00 - Metal Doors and Frames:  Coordinate installation of switches.

Specifier Note:  Strip doors can be used in conjunction with air curtains to provide an even higher level of separation.  Retain first paragraph below if required for a specific project.  Consult Berner catalog for a complete list of available strip doors.

Section 08 38 13 - Flexible Strip Doors:  Coordinate installation of strip doors with installation of air curtains.

Section 08 41 00 - Entrances and Storefronts:  Coordinate installation of switches.

Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air door must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware.

Specifier Note:  Retain any of the three following paragraphs if air curtains are mounted above ceiling.  Delete if no units installed above ceiling.

Section 09 22 16 - Non-Structural Metal Framing:  Framing and blocking above ceiling as required for installation of air curtain.

Section 09 29 00 - Gypsum Board:  Ceiling finish abutting air curtain.

Section 09 51 13 - Acoustical Panel Ceilings:  Ceiling finish abutting air curtain.

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to be field painted.  Protect electrical contracts and moveable parts from paint.

Section 09 91 00 - Painting:  Field applied finishes.

Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

REFERENCE STANDARDS

Air Movement & Control Association International, Inc. (AMCA):

          - AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.

          - AMCA 220 - Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings.

          - AMCA 222 - Application Manual for Air Curtain Units.

National Electrical Manufacturers Association (NEMA):

          - NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

NSF International (NSF):

          - NSF/ANSI 37 - Air Curtains for Entranceways in Food and Food Service Establishments.

Underwriters Laboratories (UL):

          - UL 507 - Electric Fans.

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for [____________] including:

          - [_____________________.]

          - Rated capacities.

          - Operating characteristics.

          - Accessories.

          - Options.

Shop Drawings:  Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

          - Indicate dimensions, weights, loads, clearances required, location and size of field connections.

          - Provide wiring diagrams for power, signal, and control wiring.

Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

Warranties:  Sample of special warranties.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Specifier Note:  Retain the following paragraph if specifying the ambient type of air curtain in this section.

Comply with AMCA 220, "Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings," for airflow rate, average outlet velocity, outlet velocity uniformity, velocity projection, and power rating.

Certification:

          - Unheated Units:  Certified for customer entry in accordance with NSF/ANSI 37.

          - Unheated to be UL Listed in the United States and Canada.

DELIVERY, STORAGE AND HANDLING

Deliver air curtains in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

WARRANTY

Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

          - Five-year limited warranty for unheated units.

- PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International Corporation, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

Substitutions are not permitted.

Substitutions will be considered under provisions of Section 01 60 00.

AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are required.

Acceptable Products:  Berner Sanitation Certified Low Profile 7 Model SLC08 Ambient.

Construction:  Provide factory-assembled units of sufficient structural strength to be supported from ends without intermediate support. Ship units completely assembled.

Cabinet:

Specifier Note: Retain one of the options in the following subparagraph.  Standard cabinet construction is riveted aluminized steel with white powder coated finish; optional cabinet available in stainless steel or custom color powder coated aluminized steel.

          - Material and Finish:  [Aluminized steel cabinet with stainless steel riveted construction and [white] [[insert color selection] powder coated finish.] [Stainless steel cabinet with stainless steel riveted construction.]  [Tamper-resistant construction; parts cannot be disassembled without special tool provided by manufacturer.]

          - Dimensions:  Not to exceed 8.5 in (21.6 cm) high by 8.5 in (21.6 cm) deep.

Specifier Note:  Retain only the mounting method required for a specific project in the following subparagraph and delete the others.

          - Mounting:  Provide for [wall] [suspended] mounting.

          - Service Access: Removable screen and removable bottom access panel.

Motors: 1/5-HP, 1680 rpm, single phase, 1-speed, TEAO, direct drive, resilient mounted, continuous duty, with internal thermal-overload protection and permanently lubricated sealed ball bearings.

Fans:  Balanced forward curved cross flow, tangential type, made of aluminum with flexible hubs and mounted in matched fan scrolls constructed of material used in constructing cabinet.

Discharge Nozzles:

          - Provide uniform velocity across width of air curtain.

          - Aperture:  2.375 in (6 cm) slot by width of air curtain.

Vanes: 1.5 in (3.8 cm) minimum height; constructed of airfoil-shaped aluminum extrusions; adjustable plus or minus 20 degrees to deflect airflow.

Inlet:

          - Location: Front.

          - Screen:  Perforated pattern constructed of the same material and finish used for the cabinet.

Specifier Note:  Retain the following paragraph if optional filters are required for a specific project.

Air Inlet Filter:  Flat faced fire-rated re-cleanable aluminum with integral filter brackets.

CONTROLS

Specifier Note:  Switches are not included with the unit and a provision for remote mounting is standard. Optional switches are available for remote or unit mounting.

Switching:

Specifier Note: Retain the following subparagraph if optional switch is required.

- 1.	Manual Switch:  [Factory installed “Fan On-Off” switch] [Remote Wall mounted Fan On-Off switch] [Remote mounted rotary cam HAND-OFF-AUTOMATIC Switch (Switch allows manual on-off operation or operation controlled by automatic door switch that activates unit when door opens and deactivates unit when door closes)].

Specifier Note:  Retain one of the following two paragraphs and delete the remaining one.  In the first paragraph the air curtain turns on when door is opened and shuts off when door is closed.

Basic Control Package:  Air curtain turns on when door is opened and shuts off when door is closed.

Specifier Note:  Retain either Line Voltage Control or 24V Control the following subparagraph and delete the other one.  Retain door switch type and delete the others.

- Line Voltage Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] style door switch.

- 24 Volt Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] [Magnetic reed] style door switch and factory-installed transformer.

- 120 Volt Control:  NEMA 4 Magnetic Reed door switch.

Specifier Note:  In the following paragraph the air curtain turns on when door is opened and shuts off after the door is closed and the set delay time expires.

Deluxe Control Package: Air curtain turns on when door is opened and shuts off when door is closed, unit remains on until set delay time expires.

Specifier Note:  Retain either Line Voltage Control or 24V Control the following subparagraph and delete the other one.  Where applicable retain door switch type for a specified project.

- Line Voltage Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] style door switch and factory-installed time delay.

- 24 Volt Control:  [NEMA [1] [4] plunger] [NEMA 1 roller] [Magnetic reed] style door switch and factory-installed time delay.

Specifier Note:  Retain the following paragraph if a disconnect switch is required to simplify power shut-off when servicing air curtain.

Disconnect Switch:  Provide remote mounted lockable non-fused toggle disconnects based on number of power supplies required.

Specifier Note:  Retain the following paragraph and insert text describing coordinating operational sequence of air curtain controls if required.

Sequencing:  [______________________________.]

MOUNTING ACCESSORIES

Specifier Note:  Show mounting brackets on Drawings if required.

Provide brackets and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

Specifier Note:  Retain the applicable brackets from the list below and delete those not required for a project.  Standard Wall Bracket material is galvanized steel with gray powder coated finish.  Standard Z-style bracket is stainless steel.

- Wall Brackets:  [0 to 12 in (0 to 30.5 cm)] [0 to 20 in (0 to 50.8 cm)] from [[galvanized steel with [gray] [insert color selection] powder coated finish] [stainless steel].

- Z-style Wall Bracket:  4.5 in (11.4 cm) to 7 in (17.8 cm) adjustable depth mounting bracket from [stainless steel] [[insert color selection] powder coated aluminized steel].

- EXAMINATION

EXAMINATION

Verify that the door frame and adjacent construction are installed correctly and are ready to receive work of this Section.

Verify that utilities are in correct location and are of correct capacities for specified products.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

Securely install air curtains plumb, level, and as close as practical to top of opening and face of wall.

Install switches where indicated on Drawings.

CONNECTIONS

Connect air curtain to utilities as specified in other Division 26 sections.

FIELD QUALITY CONTROL

Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Test and operate air curtain to be sure that it performs as intended.

ADJUSTING

Adjust motor and fan speed to prepare installed products to perform properly.

Specifier Note: Delete the optional text in the following paragraph if not required for a specific project.

Adjust discharge nozzles to deflect air outward [unless otherwise required].

CLEANING

Clean air curtain prior to commissioning.

Repair or repaint damage to finishes on exposed-to-view surfaces.

SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

Test and operate air curtains to ensure that they perform as intended.  Adjust discharge nozzles to deflect air outward [unless otherwise required].

DEMONSTRATION

Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2014 Berner International Corporation.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

New 12/14