SECTION 23 34 33

AIR CURTAINS

Berner Series Architectural 8 Series (AE08) air curtains (a.k.a. air doors) are designed for entry doors where an aesthetic appearance and quiet operation is desired. They are suitable for opening heights up to 8 ft (243.8 cm) for environmental separation.

Air curtains provide environmental separation at openings by reducing the infiltration of unconditioned air, fumes, dust, and humidity.  At exterior openings, they can resist winds up to 8 MPH (13 KPH) and are mounted inside the building.  Air curtains can also provide chemical-free flying insect control. During cold seasons, warm air that has risen towards ceiling is recirculated; they can also be used at interior openings such as doors to coolers or clean rooms.  Optimum protection is provided when units are mounted flush to the wall and as close to top of door opening as possible. To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

Series AE08 model air curtains have 1/5 HP electronically commutated (EC) motors and a smart controller supported by the Berner app.  They can be wall mounted or suspended from the ceiling.  They shall be installed indoors only and require – a minimum clearance of at least 6 ft (182.9 cm) between the bottom of the unit and the floor, a minimum of 4 in (10.2 cm) between the top of the unit and the ceiling and 1 in (2.5 cm) between the sides and any combustible material.

Edit guide specification to include only information specific to your project.  Delete or add text, select appropriate bracketed phrases, and fill in blanks as required.  Go to Berner catalog or website to select specific models and sizes that are required for project and to obtain data necessary to edit this specification section.

Coordinate specification with information shown on project drawings and schedules.  In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules.  Cross check mechanical and architectural drawings.

This guide specification is available in word processing format at www.berner.com.  Turn on “Hidden Text” function in your word processor to display “Specifier Notes.”

For additional information or name of Berner representative in your area, call Berner International at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.berner.com. A selection guide is available at www.berner.com to suggest models appropriate for typical applications.

GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

Air curtains [, electric heated] [, hot water heated].

[Insert item description.]

RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note: If switches for air curtains are mounted on door frames, retain either Section 08 11 00 or 08 41 00 below to facilitate coordination.

Section 08 11 00 - Metal Doors and Frames:  Coordinate installation of switches.

Section 08 41 00 - Entrances and Storefronts:  Coordinate installation of switches.

Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air curtain must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware.

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to be field painted.  Protect electrical contacts and moveable parts from paint.

Section 09 91 00 - Painting:  Field applied finishes.

Specifier Note:  Retain the following paragraph if hot water heaters are used in air curtain.

Division 22 - Plumbing:  Connection of hot water supply to heater used in air curtain.

Division 23 - Heating, Ventilating, and Air-Conditioning (HVAC):  Connection of hot water supply to coil used in air curtain.

Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

REFERENCE STANDARDS

Specifier Note:  Retain the following paragraph and subparagraph if steam or hot water heated units are required for a specific project.

Air Conditioning & Refrigeration Institute (ARI):

          - ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

Specifier Note:  Retain the following paragraph and subparagraph if BACnet communication interface is required for a specific project.

American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE):

          - ASHRAE 135 - BACnet - A Data Communication Protocol for Building Automation and Control Networks.

          - ASHRAE 135.1 - Method of Test for Conformance to BACnet

Air Movement & Control Association International, Inc. (AMCA):

          - AMCA 211 - Certified Ratings Program - Product Rating Manual for Fan Air Performance.

          - AMCA 220 - Laboratory Methods of Testing Air Curtain Units for Aerodynamic Performance Ratings.

          - AMCA 222 - Application Manual for Air Curtain Units.

National Electrical Manufacturers Association (NEMA):

          - NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

Underwriters Laboratories (UL):

          - UL 507 - Electric Fans.

          - UL 2021 - Fixed and Location-Dedicated Electric Room Heaters.

          - UL 1995 - Heating and Cooling Equipment

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for [____________] including:

          - [_____________________.]

          - Rated capacities.

          - Operating characteristics.

          - Accessories.

          - Options.

Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

          - Indicate dimensions, weights, loads, clearances required, location and size of field connections.

          - Provide wiring diagrams for power, signal, and control wiring.

Operation and Maintenance Data:  Manuals for air curtain operation and maintenance.

Warranties:  Sample of special warranties.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Aerodynamic Performance: Test units in accordance with AMCA 220, "Laboratory Methods of Testing Air Curtains for Aerodynamic Performance Ratings," for airflow rate, average outlet velocity, outlet velocity uniformity, velocity projection, and power rating.

Certification:

          - Provide units with AMCA Certified Ratings Seal.

          - UL and cUL listed to comply with applicable United States and Canadian standards.

Specifier Note:  Retain the following paragraph if specifying an air curtain with BACnet communication interface.

          - BACnet Testing laboratories (BTL) Certificate of Conformance

Specifier Note:  Retain the following paragraph if specifying an air curtain with a hot water coil.

Comply with ARI 410 for components, construction, and rating.

          - Certify coils in accordance with ARI 410.

DELIVERY, STORAGE AND HANDLING

Deliver air curtains in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

WARRANTY

Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

Specifier Note:  Retain either of the following two subparagraphs to agree with type of unit selected for a project and delete the other. Retain both subparagraphs if project has both types of units.

          - Five-year limited warranty for unheated (ambient) units.

          - Two-year limited warranty for heated units.

PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International LLC, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

Substitutions are not permitted.

Substitutions will be considered under provisions of Section 01 60 00.

AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are not required.

Acceptable Products:  Berner Architectural Elite 8 Model [AE08 Ambient] [AE08 Electric Heated] [AE08 Hot Water Heated].

Construction:  Provide factory-assembled units of sufficient structural strength to be supported from ends without intermediate support.  Ship units completely assembled.

Cabinet:

Specifier Note: Retain one of the options in the following subparagraph. Standard cabinet construction is stainless steel with an exterior bottom panel of clear satin anodized aluminum; optional white aluminum, custom color powder coated finish or stainless steel available.

          - Material and Finish:  Grade 304 or better brushed stainless steel cabinet with clear satin anodized aluminum [white aluminum] [stainless steel] [[insert color selection] powder coated] [bronze anodized aluminum] bottom panel.

Specifier Note: Retain optional text in the following subparagraph as required for the specific project.

          - Optional Décor for top mounting:  Equip air curtain with [matching material and finish as bottom panel] [Grade 304 or better brushed stainless steel] [clear satin anodized aluminum] [white aluminum] [[insert color selection] powder coated] decorative rear cover plate to hide fasteners.

Specifier Note: Retain one of the options in the following subparagraph and delete the other.

          - Dimensions:  Not to exceed 10.75 in (27.3 cm) high by [22.93 in (58.2 cm) standard depth] [23.62 in (60.0 cm) deep including mounting plate].

Specifier Note:  Retain only the mounting method required for a specific project in the following subparagraph and delete the others.

          - Mounting:  Provide for wall and suspended mounting.

          - Service Access: Removable screen and bottom access panel.

Motors:  1/5-HP, 1800 RPM, single phase, variable speed, EC, direct driven, resilient mounted, continuous duty, with internal thermal-overload protection and permanently lubricated sealed ball bearings.

Fans:  Balanced forward curved cross flow tangential type, made of aluminum with flexible hubs and mounted in matched fan scroll made of aluminized steel.

Discharge Nozzles:

          - Provide uniform velocity across width of air curtain.

          - Aperture:  2.25 in (5.715 cm) slot by width of air curtain.

Vanes:  1.50 in (3.8 cm) minimum height; articulating construction of airfoil-shaped aluminum extrusions; adjustable plus or minus 20 degrees to deflect airflow.

Inlet:

          - Location:  Top.

          - Screen:  Perforated pattern of the same material and finish used for the cabinet.

          - Inlet Filter:  Flat faced fire-rated re-cleanable aluminum with integral bracket.

Specifier Note:  Retain the following article if heated units are required for a specific project.

HEATING ELEMENTS

Electric Heating Coil:  UL-approved, factory-mounted, factory-wired, thermally-protected, in galvanized steel frame.

          - Single stage, intake mounted, open element helical coil with point suspension to minimize air turbulence, [single] [three] phase circuit.

          - Thermal Cutout:  Locks out electric heater when prolonged abnormal over-temperature conditions exist.

Hot Water Coil:  Certified in accordance with ARI 410; 16-gage galvanized steel casing, 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins and seamless copper headers.

          - Characteristics:  Design to operate at maximum 250-psig (1720-kPa) and 300 degrees F (149 degrees C) hot water.

          - Leak-test under water at 350-psig (2415-kPa) dry nitrogen.

          - Factory mount coil on air intake and protect with perforated metal screen.

CONTROLS

Controller:

          - UL listed, industrial type, pre-wired, with solid-state control switch.

Specifier Note: AE08 units are supplied standard with an IntelliswitchTM digital programmable controller.  Unit mounted display is standard.

          - Factory-mounted and wired IntelliswitchTM digital programmable controller with the following features:

5 volt DC output for external door and thermostat sensors.

Lock and Unlock tamperproof feature.

EC Motor control signal suitable for 10 fan speed settings.

Programmable fan start and fan stop time with provisions to set the start and stop times for any day of the week.

Programmable settings for all user controlled options.

Adjustable time delay from 0 to 10 minutes.

Four (4) preset and three (3) customizable programs - On, Off, Automatic, Comfort Plus, Program 1, Program 2, and Program 3.

Built-in capillary style thermostat for heated units with temperature settings of 34 degrees F to 90 degrees F (1 degree C to 32 degrees C).

Comfort Plus heating mode calls for heat and fan.

Emergency stop.

Clock with lighted display.

Ability to be operated via Mobile App.

Specifier Note: AE08 units are supplied with wireless control via mobile app with IntelliswitchTM digital programmable controller.

Wi-Fi and BLE Communication: Native Wi-Fi and Bluetooth wireless networking included with the IntelliswitchTM digital programmable controller for use with Berner Air mobile app to allow for remote control of air curtain via smart phone, tablet and/or BACnet client.

Specifier Note: AE08 units allow for either a wireless or a wired BACnet connection to the Building Management System (BMS). Retain the following subparagraph if the AE08 unit will be connected to a BMS.

          - Supply BACnet client connection: [over Wi-Fi] [via CAT 5 cable connected to air curtain]

Specifier Note:  Retain the following subparagraph if remote-mounted control option is required for a specific project.

Wall-mounted touchscreen:  Commercial-grade [black] [white] wall-mounted touchscreen for use with IntelliswitchTM digital programmable controller and wireless communication powered by CAT 5 cable connected to air curtain.

Specifier Note:  Retain the following subparagraph if an automatic door switch is required for a specific project.  An automatic door switch automatically activates unit when door opens and deactivates unit when door closes.

Door Switch:  [[white] [brown] magnetic reed] [NEMA [1] [4] plunger] [NEMA 1 roller] style door switch.

Specifier Note:  Retain the following paragraph when specifying heated units and an additional temperature measurement point is desired beyond that of the intake air from the unit mounted thermostat.

Thermostat:  For remote mounted sensing to prevent the operation of heater when inside air temperature exceeds desired temperature.

Specifier Note:  Retain the following paragraph if a disconnect switch is required to simplify power shut-off when servicing air curtain.

Disconnect Switch:  Provide lockable factory mounted non-fused toggle disconnects based on number of power supplies required.

Specifier Note:  Retain the following paragraph and insert text describing coordinating operational sequence of air curtain controls if required.

Sequencing:  [______________________________.]

MOUNTING ACCESSORIES

Specifier Note:  Show mounting brackets on Drawings if required.

Provide brackets and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

          - Wall Mounting Hardware:  Cabinet brackets, wall mounting plates and fasteners to assemble and allow flexible installation across the width of the unit on suitable load bearing wall component(s).

EXECUTION

EXAMINATION

Verify that door frame and adjacent construction are installed correctly and are ready to receive work of this Section.

Verify that utilities are in correct location and are of correct capacities for specified products.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

Securely install air curtains plumb, level, and as close as practical to top of opening and face of wall.

Install switches where indicated on Drawings.

CONNECTIONS

Specifier Note:  Retain the appropriate option in the following paragraph depending on type of air curtain(s) retained in Part 2 - Products and delete those not used.

Connect air curtain to utilities as specified in [Division 22] [Division 23] [Division 26] sections.

FIELD QUALITY CONTROL

Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Test and operate air curtain to be sure that it performs as intended.

ADJUSTING

Adjust fan speed to prepare installed products to perform properly.

Specifier Note:  Delete the optional text in the following paragraph if not required for a specific project.

Adjust discharge nozzles to deflect air outward [unless otherwise required].

CLEANING

Clean air curtain prior to commissioning.

Repair or repaint damage to finishes on exposed-to-view surfaces.

SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

Test and operate air curtains to ensure that they perform as intended.  Adjust discharge nozzles to deflect air outward [unless otherwise required].

DEMONSTRATION

Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2020 Berner International LLC.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.