SECTION 23 34 33

AIR CURTAINS

### Berner RevolvAirTM Air Curtain Systems for Revolving Doors (RevolvAir) are designed to work with Revolving Doors to protect the interior of the building from the air brought into the space via the revolving door chambers.  Mounted on the interior side of the building, on top of the Revolving Door system, the RevolvAir is suitable for opening heights up to 12 ft (365.8 cm) for environmental separation.

### Air curtains provide environmental separation at openings by reducing the infiltration of unconditioned air, fumes, dust, and humidity.  At exterior openings, they are generally mounted inside the building. During cold seasons warm air that has risen towards ceiling and stratified is recirculated improving room temperature uniformity.  Optimum protection is provided when the discharge nozzle is mounted as close to top of door opening as possible.   To ensure peak performance keep air stream free of obstructions.  Air curtains may not be fully effective where negative air pressure exists on one side of door; contact Berner for additional information.

### The RevolvAir model air curtain systems have 1/2 HP motor(s), a digital controller, a transition plenum and a discharge plenum.  The system may be mounted on top of the revolving door system (which shall be verified by the door manufacturer), wall mounted, or suspended from the ceiling. All units shall be installed indoors only and require a minimum clearance of at least 1 in (2.5 cm) between the bottom of the unit and the top of the revolving door, a minimum of 12 in (30.48 cm) between the intake and any surface and 1 in (2.5 cm) between the sides and any combustible material.

### Edit guide specification to include only information specific to your project.  Delete or add text, select appropriate bracketed phrases, and fill in blanks as required.  Go to www.berner.com to select specific models and sizes that are required for project and to obtain data necessary to edit this specification section.

### Coordinate specification with information shown on project drawings and schedules.  In general, drawings indicate locations of air curtains and switches and special mounting requirements, while sizes and capacities of air curtains and utilities should be described in specifications or schedules.  Cross check mechanical and architectural drawings.

### This guide specification is available in word processing format at www.berner.com.

For additional information or name of Berner representative in your area, call Berner International at 800-245-4455 in U.S. or 800-242-4455 in Canada, or visit www.berner.com. A selection guide is available at www.berner.com to suggest models appropriate for typical applications.

GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 01 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section. Retain only those options in the first paragraph below that are required for a specific project.

    - Air curtains[, electric heated] [, hot water heated] [, steam heated]

[Insert item description.]

Transition Plenum

Discharge Plenum

Trim Package

RELATED REQUIREMENTS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 04 22 00 - Concrete Unit Masonry:  Blocking or reinforcing in wall as required for attachment of air curtain.

Section 05 40 00 - Cold-Formed Metal Framing:  Reinforcing in wall as required for attachment of air curtain.

Section 06 10 00 - Rough Carpentry:  Blocking in wall as required for attachment of air curtain.

Specifier Note: If switches for air curtains are mounted on door frames, retain either Section 08 11 00 or 08 41 00 below to facilitate coordination.

Section 08 11 00 - Metal Doors and Frames:  Coordinate installation of switches.

Section 08 41 00 - Entrances and Storefronts:  Coordinate installation of switches.

Specifier Note:  Retain the following paragraph if door openers or automatic door opening assemblies are used.  Air door must be positioned so air stream is not obstructed when deflected 20 degrees to either side of centerline.  If air stream strikes any obstruction (top edge of the doorway, door opening device, etc.) effectiveness of unit will be reduced.

Section 08 71 00 - Door Hardware:  Coordinate with installation of hardware.

Specifier Note:  Retain any of the three following paragraphs if air curtains are suspension mounted above ceiling.  Delete if no units installed suspended from the ceiling.

Section 09 22 16 - Non-Structural Metal Framing:  Framing and blocking above ceiling as required for installation of air curtain.

Section 09 29 00 - Gypsum Board:  Ceiling finish abutting air curtain.

Section 09 51 13 - Acoustical Panel Ceilings:  Ceiling finish abutting air curtain.

Specifier Note:  Retain the first paragraph below if air curtain cabinets are to be field painted.  Protect electrical contacts and moveable parts from paint.

Section 09 91 00 - Painting:  Field applied finishes.

Specifier Note:  Retain the following paragraph if hot water heaters are used in air curtains.

Division 22 - Plumbing:  Connection of hot water supply to heater used in air curtains.

Specifier Note:  Retain the following paragraph if steam heaters are used in air curtains.

Division 23 - Heating, Ventilating, and Air-Conditioning (HVAC):  Connection of steam supply to heater used in air curtains.

Division 26 - Electrical:  Connection of electrical service and controls.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

REFERENCE STANDARDS

Specifier Note:  Retain the following paragraph and subparagraph if steam or hot water heated units are required for a specific project.

Air Conditioning & Refrigeration Institute (ARI):

ARI 410 - Forced-Circulation Air-Cooling and Air-Heating Coils.

National Electrical Manufacturers Association (NEMA):

NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum).

Underwriters Laboratories (UL):

UL 507 - Electric Fans.

UL 508 - Industrial Control Equipment.

UL 2021 - Fixed and Location-Dedicated Electric Room Heaters.

UL 1995 - Heating and Cooling Equipment

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01 33 00] [______].

Product Data:  Submit for [____________] including:

[_____________________.]

Rated capacities.

Operating characteristics.

Accessories.

Options.

Shop Drawings:  For air curtain components not adequately described by product data.  Show configuration of non-standard units.  Include plans, elevations, sections, details, and attachments to other work.

Indicate dimensions, weights, loads, clearances required, location and size of field connections.

Provide wiring diagrams for power, signal, and control wiring.

Operation and Maintenance Data:  For air curtains to include in maintenance manuals.

Warranties:  Sample of special warranties.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of air curtains of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide air curtains produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of air curtain through one (1) source from a single manufacturer.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Certification:

Unheated and electric heated air curtain units to be UL Listed in the United States and Canada.

Specifier Note:  Retain the following paragraph if specifying the steam or hot water type of air curtain in this section.

Comply with ARI 410 for components, construction, and rating.

Certify coils in accordance with ARI 410.

DELIVERY, STORAGE AND HANDLING

Deliver air curtain systems in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

WARRANTY

Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of air curtains that fail in materials or workmanship within specified warranty period.

Specifier Note:  Retain either of the following two subparagraphs to agree with type of unit selected for a project and delete the other. Retain both subparagraphs if project has both types of units.

Five-year limited warranty for unheated units.

Two-year limited warranty for heated units.

PRODUCTS

MANUFACTURERS

Basis-of-Design Manufacturer:  The design for air curtains is based on products manufactured by Berner International LLC, 111 Progress Avenue, New Castle; PA, Telephone: 724-658-3551; Toll-Free Telephones: 800-245-4455 (U.S.), 800-242-4455 (Canada); Fax: 724-652-0682; email: airdoors@berner.com; Website: www.berner.com.

Specifier Note:  Retain one of the following two paragraphs and delete the other.

Substitutions are not permitted.

Substitutions will be considered under provisions of Section 01 60 00.

AIR CURTAINS

Specifier Note: Retain model types in the following paragraph as required for specific project. Delete those that are required.

Acceptable Products:  Berner RevolvAir Model [RVC Ambient] [RVC Electric Heated] [RVC Hot Water Heated] [RVC Steam Heated].

Construction:  Provide factory-assembled air curtain units of sufficient structural strength to be supported from ends without intermediate support along with a transition and discharge plenum.  Ship air curtain units completely assembled.  Ship transition plenum completely assembled.  Ship discharge plenum completely assembled.

Cabinet:

Specifier Note: Retain one of the options in the following subparagraph. Standard construction is welded aluminized steel with powder coated white finish; optional construction in stainless steel (grade 304 or better) or custom color powder coated aluminized steel. Select from two types of systems: Concealed Air Curtain System (air curtain is mounted over top of the revolving door and hidden from view by transition plenum and discharge plenum); Exposed Air Curtain System (air curtain is mounted over top of the revolving door and placement of transition plenum and discharge plenum allow view of air curtain).

[Concealed] [Exposed] Air Curtain System comprised of air curtain, [transition plenum] and discharge plenum(s).

Material and Finish: Air curtain: minimum 16-gauge [aluminized steel base frame with mill aluminum inlet screen and access panels with [white] [insert color selection] powder coated finish] [stainless steel base frame, access panels and [mill aluminum] [stainless steel] screen] welded construction.

Dimensions: Air curtain cabinet (not including external heating options) not to exceed 18 in. (45.7 cm) high by 15 in. (38.1 cm) deep by [39 in. (99.1 cm)] [75 in. (190.5 cm)] [ 102 in. (259.1)] wide.

Specifier Note:  Retain only the mounting method required for a specific project in the following subparagraph and delete the others.

Mounting:  Provide for [top of revolving door system] [wall] [suspension] mounting.  Include vibration isolation kit for systems mounted on and/or touching the top of Revolving Door.

Service Access: Removable screen, top or side access panels.

Motors:  1/2-HP, 1680 RPM, single phase, variable speed, ODP, direct drive, resilient mounted, continuous duty, with internal thermal-overload protection and permanently lubricated sealed ball bearings.

Fans:  Balanced forward curved centrifugal type, double inlet, mounted in matched fan housings with aerodynamically formed air inlet venturis.  Manufacture wheels and housings from galvanized steel.

Specifier Note:  Retain the following article if a Transition Duct is required.

Transition Plenum:

- Material and Finish: Minimum 16-gauge [aluminized steel with [white] [insert color selection] powder coated finish] [stainless steel] mechanically fastened construction.

- Dimension: not to exceed 5.13 in. (13.0 cm) high by [insert depth] by [39 in. (99.1 cm)] [75 in. (190.5 cm)] [ 102 in. (259.1)] wide.

Discharge Plenum:

Material and Finish: minimum 22-gauge [aluminized steel with [white] [insert color selection] powder coated finish] [stainless steel] mechanically fastened construction with 3.0 in. (7.6 cm) aluminum airfoil vanes equally spaced for uniform air distribution.

Dimension: Aperture opening 2.5 in (6.4 cm) slot by arc length [equal to opening + 4” for 2” overlap of end posts] [specify length greater than the opening] of the revolving door. [Specify height] of [concealed] [exposed] from top of revolving door opening to top of plenum to mount [on top] [in front] of revolving door assembly. Approval drawing shall be provided and approved by the manufacturer.

Provide uniform velocity across width of air curtain discharge.

Specifier Note:  Retain the following article if a façade wrap Trim Package, mounted over over the top of the front of the discharge plenum, is required.

Trim Package, Material and Finish: [22 gauge steel [insert color selection] aluminized steel powder coated finish] [22 gauge brushed finish stainless steel] [[satin clear] [bronze] anodized aluminum] [white polyester painted aluminum].

Specifier Note:  Retain one of the following options based on the type of air curtain system selected in Paragraph 2.2.C. Concealed systems only available with Back air intake; Exposed systems available with Back or Top air intake.

Inlet (Air Intake):

Location: [Back] [Top].

Specifier Note:  Retain the option that is required after editing the material and finish type in Paragraph 2.2.C above and delete the others.

Screen:  Perforated pattern [mill aluminum] [stainless steel] painted to match cabinet with border.

Specifier Note:  Retain the following paragraph optional filters are required for a specific project. Select desired filter type and delete the others.

Air Inlet Filter:  [Flat-faced re-cleanable aluminum] [Flat-faced re-cleanable polyester with aluminum frame] [with screen] [without screen].

Specifier Note:  Retain the following article if heated units are required for a specific project.

HEATING ELEMENTS

Electric Heating Coil:  UL-approved, factory-mounted, factory-wired, thermally-protected, galvanized steel frame.

Venturi mounted helical coil with point suspended elements, [single] [three] phase circuit.

Thermal Cutout: Locks out electric heaters when prolonged abnormal over-temperature conditions exist.

Steam Coil: Certified in accordance with ARI 410; constructed from 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins.

Characteristics:  Design to operate at maximum 150-psig (1035-kPa) and 366 degrees F (185 degrees C) steam.

Leak-test under water at 350-psig (2410-kPa) dry nitrogen.

Factory mount coil on air intake and protect with perforated metal screen.

Hot Water Coil:  Certified in accordance with ARI 410; constructed from 5/8-inch (15.8 mm) outside diameter copper tube with aluminum fins.

Characteristics:  Design to operate at maximum 250-psig (1720-kPa) and 300 degrees F (149 degrees C) hot water.

Leak-test under water at 350-psig (2410-kPa) dry nitrogen.

Factory mount coil on air intake and protect with perforated metal screen.

CONTROLS

Wiring Compartment:

Specifier Note: Single power supply is standard on unheated and hot water/steam heated units.  Electric heated units have single or multiple power supplies based on voltage and kW rating.

[Multiple] [Single] power supply.

Specifier Note:  Retain the Type 4X enclosure in areas subject to corrosive or wash-down type conditions and delete the first option.

Enclosure:  Oil-tight and dust-tight NEMA Type [4/12] [corrosion resistant NEMA 4X [polycarbonate] [stainless steel]] enclosure with neoprene door gasket.

Mounting:  Unit mounted [right end] [left end].

Specifier Note:  Retain the following paragraph if a disconnect switch is required to simplify power shut-off when servicing air curtain.  Delete the following subparagraph if this option is not selected for a specific project. Panel mounted rotary disconnect only available for control panels with a single circuit.

Disconnect Switch:  Provide lockable [[remote] [unit] mounted non-fused toggle disconnects based on number of power supplies required] [panel mounted through the door rotary [fused] [non-fused] disconnect].

Controller

Specifier Note: RVC units are supplied standard with an IntelliswitchTM digital programmable controller.  Remote mounted display is standard.

UL Listed factory-mounted and wired IntelliswitchTM digital programmable controller with the following features:

5 volt DC output for control circuit.

Lock and Unlock tamperproof feature.

Motor and switching suitable for 10 fan speed settings.

Programmable fan start and fan stop time with provisions to set the start and stop times for any of the week.

Programmable settings for all user controlled options.

Adjustable time delay from 0 to 10 minutes.

Five (5) preset and three (3) customizable programs - On, Off, Automatic, Deluxe, Comfort Plus, Program 1, Program 2, and Program 3.

Fan fail lockout.

Built-in capillary style thermostat for heated units with temperature settings of 34 degrees F to 90 degrees F (one (1) degree C to 32 degrees C).

Two (2) heating modes, one (1) call for heat and one (1) call for fan and heat.

Emergency stop.

Clock with lighted display.

Ability to be operated via Mobile App with Wi-Fi Controller option.

[Unit mounted display] [Remote mounted display with 20 ft (6.1m cable].

Specifier Note:  Retain the following Wi-Fi control via mobile APP option with IntelliswitchTM digital programmable controller if required for a specific project

A.	Wi-Fi Controller: controller for use with IntelliswitchTM digital programmable controller and Mobile Berner APP to allow for remote control of the air curtain(s) via smart phone or tablet.

Specifier Note:  Retain the following subparagraph if a door sensor is required for a specific project.  A door motion sensor automatically activates unit when door moves and deactivates unit when door stops.

Door Activation:  [Motion sensor] [Interlocked with [door sensor] [Building Management System].

Specifier Note:  Retain the following remote control option with IntelliswitchTM digital programmable controller if required for a specific project.

Remote Control:  Infra-red controller for use with IntelliswitchTM digital programmable controller.

Specifier Note:  Retain the following paragraph when specifying electric heated units. The IntelliswitchTM comes standard with a built-in temperature sensing probe add an additional thermostat for remote sensing.

Thermostat:  For remote mounted sensing to prevent the operation of heater when inside air temperature exceeds desired temperature.

Specifier Note:  Retain the following paragraph and insert text describing coordinating operational sequence of air curtain controls if required.

Sequencing:  [______________________________.]

MOUNTING ACCESSORIES

Specifier Note:  Show mounting brackets on Drawings if required.

Provide brackets and other mounting accessories as required to permit installation and proper functioning of air curtain to meet project conditions of use.

Specifier Note:  Retain the applicable brackets from the list below and delete those not required for a project. Standard wall bracket material is galvanized steel with gray powder coated finish; optional in stainless steel or custom color powder coated galvanized steel.

Wall Brackets:  [0-12 in (0-30.5 cm)] [0-20 in (50.8 cm)] from [[galvanized steel with [gray] [insert color selection] powder coated finish] [stainless steel] structural channel.

EXECUTION

EXAMINATION

Verify that the revolving door and adjacent construction are installed correctly and are ready to receive work of this Section.  If mounting by resting the RevolvAir on top of the revolving door, verify that the structure will bear the weight of the RevolvAir.

Verify that utilities are in correct location and are of correct capacities for specified products.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Specifier Note: Delete the optional text in the following paragraph if shop drawings are not required for a specific project.

Install air curtains where indicated on Drawings and accordance with [shop drawings and] manufacturer’s instructions.  Provide clearance to permit servicing and maintenance.

Securely install air curtain units plumb, level, and as close as practical to top of revolving door canopy opening.

Install switches where indicated on Drawings.

CONNECTIONS

Specifier Note:  Retain the appropriate option in the following paragraph depending on type of air curtain(s) retained in Part 2 - Products and delete those not used.

Connect air curtain to utilities as specified in [Division 22] [Division 23] [Division 26] sections.

FIELD QUALITY CONTROL

Provide a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Test and operate air curtain to be sure that it performs as intended.

ADJUSTING

Adjust fan speed to prepare installed products to perform properly.

CLEANING

Clean air curtain prior to commissioning.

Repair or repaint damage to finishes on exposed-to-view surfaces.

SYSTEM STARTUP

Specifier Note:  Retain optional text in paragraph below if required for a specific project.

Test and operate air curtains to ensure that they perform as intended.  Adjust system speed such that discharge air strikes the floor with enough energy to split but not turbulence enough to force unconditioned outside air to escape from the revolving door pocket.

DEMONSTRATION

Demonstrate for Owner’s maintenance personnel how to adjust, operate, and maintain air curtains.

END OF SECTION

© 2018 Berner International Corporation.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Revised 05/2018